Strona wtórna:

1103 Measurement: Full Scale Voltage (100%) 220,0 kV

1104 Measurement: Full Scale Current (100%) 1200 A

1105 Line Angle 82 °

1211 Angle of inclination, distance charact. 82 °

1111 Line Length 47 km

1116 Zero seq. comp. factor RE/RL for Z1 0,00

1117 Zero seq. comp. factor XE/XL for Z1 0,50

1118 Zero seq. comp.factor RE/RL(> Z1) 0,00

1119 Zero seq. comp.factor XE/XL(> Z1) 0,00

k0 = 0,4951 (dopisał RL)

fi_k0 = 8 st. (dopisał RL)

k1,2 = 0 (dopisał RL)

fi_k1,2 = -82 st (dopisał RL)

1301 Operating mode Z1 Forward

1302 R(Z1), Resistance for ph-ph-faults 8,00 Ohm

1303 X(Z1), Reactance 8,95 Ohm

1304 RE(Z1), Resistance for ph-e faults 22,00 Ohm

1351 Operating mode Z1B (overrreach zone) Forward

1352 R(Z1B), Resistance for ph-ph-faults 8,50 Ohm

1353 X(Z1B), Reactance 12,11 Ohm

1354 RE(Z1B), Resistance for ph-e faults 22,50 Ohm

1311 Operating mode Z2 Forward

1312 R(Z2), Resistance for ph-ph-faults 9,00 Ohm

1313 X(Z2), Reactance 15,93 Ohm

1314 RE(Z2), Resistance for ph-e faults 23,00 Ohm

1321 Operating mode Z3 Forward

1322 R(Z3), Resistance for ph-ph-faults 11,00 Ohm

1323 X(Z3), Reactance 36,22 Ohm

1324 RE(Z3), Resistance for ph-e faults 24,00 Ohm