Strona wtórna:

1103 Measurement: Full Scale Voltage (100%) 220,0 kV

1104 Measurement: Full Scale Current (100%) 600 A

1105 Line Angle 80 °

1211 Angle of inclination, distance charact. 80 °

1111 Line Length 181,8 km

1116 Zero seq. comp. factor RE/RL for Z1 1,02

1117 Zero seq. comp. factor XE/XL for Z1 0,60

1118 Zero seq. comp.factor RE/RL(> Z1) 0,85

1119 Zero seq. comp.factor XE/XL(> Z1) 0,50

1301 Operating mode Z1 Forward

1302 R(Z1), Resistance for ph-ph-faults 24,850 Ohm

1303 X(Z1), Reactance 16,585 Ohm

1304 RE(Z1), Resistance for ph-e faults 66,000 Ohm

1351 Operating mode Z1B (overrreach zone) Forward

1352 R(Z1B), Resistance for ph-ph-faults 37,300 Ohm

1353 X(Z1B), Reactance 24,880 Ohm

1354 RE(Z1B), Resistance for ph-e faults 99,500 Ohm

1311 Operating mode Z2 Forward

1312 R(Z2), Resistance for ph-ph-faults 37,300 Ohm

1313 X(Z2), Reactance 24,880 Ohm

1314 RE(Z2), Resistance for ph-e faults 99,500 Ohm

1321 Operating mode Z3 Forward

1322 R(Z3), Resistance for ph-ph-faults 55,500 Ohm

1323 X(Z3), Reactance 37,100 Ohm

1324 RE(Z3), Resistance for ph-e faults 110,000 Ohm