Strona wtórna:

1103 Measurement: Full Scale Voltage (100%) 220,0 kV

1104 Measurement: Full Scale Current (100%) 1200 A

1105 Line Angle 80 °

1211 Angle of inclination, distance charact. 85 °

1111 Line Length 96,5 km

1116 Zero seq. comp. factor RE/RL for Z1 1,38

1117 Zero seq. comp. factor XE/XL for Z1 0,40

1118 Zero seq. comp.factor RE/RL(> Z1) 1,38

1119 Zero seq. comp.factor XE/XL(> Z1) 0,40

1301 Operating mode Z1 Forward

1302 R(Z1), Resistance for ph-ph-faults 15,000 Ohm

1303 X(Z1), Reactance 18,580 Ohm

1304 RE(Z1), Resistance for ph-e faults 22,000 Ohm

1351 Operating mode Z1B (overrreach zone) Forward

1352 R(Z1B), Resistance for ph-ph-faults 15,000 Ohm

1353 X(Z1B), Reactance 25,000 Ohm

1354 RE(Z1B), Resistance for ph-e faults 22,000 Ohm

1312 R(Z2), Resistance for ph-ph-faults 18,000 Ohm

1313 X(Z2), Reactance 27,820 Ohm

1314 RE(Z2), Resistance for ph-e faults 24,000 Ohm

1321 Operating mode Z3 Forward

1322 R(Z3), Resistance for ph-ph-faults 20,000 Ohm

1323 X(Z3), Reactance 43,090 Ohm

1324 RE(Z3), Resistance for ph-e faults 26,000 Ohm

1331 Operating mode Z4 Forward

1332 R(Z4), Resistance for ph-ph-faults 20,000 Ohm

1333 X(Z4), Reactance 81,820 Ohm

1334 RE(Z4), Resistance for ph-e faults 26,000 Ohm